### SECTION 26 05 33 - ELECTRICAL BUSWAY DISTRIBUTION SYSTEM

Part 1 – General

1.1 SUMMARY
A. This section includes the busSTRUT track busway system designed for lighting, power distribution, and accessory integration.

1.2 REFERENCES
A. NEC (National Electrical Code) Article 368 - Busways
B. UL 857 - Standard for Busways
C. Title 24 - Energy Code Compliance

1.3 SUBMITTALS
A. Product Data: For busSTRUT busway systems, including crossovers, jumpers, joiners, and mounting hardware.
B. Shop Drawings: Indicate busway runs and accessories.
C. Certifications: Manufacturer’s compliance with UL and NEC standards.

1.4 QUALITY ASSURANCE
A. Manufacturer Qualifications: Manufacturer with at least 10 years’ experience in manufacturing pre-wired busway systems.
B. Testing: All busways are factory-tested to ensure compliance with design specifications.

1.5 WARRANTY
A. busSTRUT's standard warranty for busway systems, covering defects in materials and workmanship for a minimum of one year.

Part 2 – Products

2.1 MANUFACTURERS
A. Approved Manufacturer: busSTRUT, 4787 Roberts Rd., Columbus, Ohio, 43228.
B. Product Line: Single-Deck and Double-Deck Busway Systems and busSTRUT READY ATTACHMENTs.

2.2 SYSTEM DESCRIPTION
A. The busSTRUT system is a modular, pre-wired power distribution busway designed for suspended installation in both open and closed ceilings.
B. Available in single-deck and double-deck configurations, supporting lighting, power, data, and decorative elements.

2.3 SYSTEM PERFORMANCE REQUIREMENTS
A. Electrical Rating:

- Voltage: Up to 277V

- Current: 20A and 40A circuits

- Single-Deck up to 80amps total

- Double-Deck up to 160amps total.

B. Finish Options: Galvanized steel, White, Black, and Sleeved Copper.
C. Custom Lengths: Available in standard lengths of 2.5’, 5’, and 10’, with options for custom lengths.

2.4 COMPONENTS
A. Busway

- 12-gauge steel, 1-5/8” x 1” for single-deck, and 1-5/8” x 2” for double-deck.

- Plug-and-play connectors for power and lighting, eliminating the need for field wiring.
B. Crossovers

- Mechanical connection for intersecting busways. Available in Slimline and Coreline configurations for both perpendicular and angled intersections.
C. Jumpers

- Electrical connectors for intersections of busway lengths. Flexible cables for accommodating various intersection configurations.
D. Power Drops

- Movable power drops that ensure straight hanging, facilitating clean and uncluttered installations.

2.5 MOUNTING HARDWARE
A. Hangers: Pre-assembled hangers for both single and double-deck busways. Options for cable glide and rigid mount systems.
B. Joiners and Crossovers: Electrical and mechanical connectors for abutting and perpendicular lengths of busway.

Part 3 – Execution

3.1 INSTALLATION
A. Install busSTRUT systems per manufacturer’s guidelines and in compliance with NEC standards.
B. Ensure all connections, including jumpers and crossovers, are properly seated and secured.

3.2 FIELD QUALITY CONTROL
A. Perform tests for continuity and load testing after installation to verify the system is correctly installed and operational.